## Calculator
HVAC CONDENSATE CALCULATOR
| Input Conditions |  | Output Conditions
| Avg DailyTemp | 70 | Temp | 55
| Avg Daily % RH | 71 | % RH | 40
| SH in gr/ft3 | 5.7595 | SH in gr/ft3 | 1.8636
| Difference in Specific Humidity gr/ft3 |  |  | 3.8959
| Percentage of Outside Air |  |  | 20%
| Tonnage of System |  |  | 3.5
Note: Assumption is 350 ft3per minute per ton
| Gallons per Minute |  |  | 0.0081847
| Gallons per Hour |  |  | 0.49108
| Gallons per Day |  |  | 11.786

## Water Vapor Capacity Table
Temperature | Grains
30 | 1.9
40 | 2.9
50 | 4.1
60 | 5.7
70 | 8
80 | 10.9
90 | 14.7
100 | 19.7
Source: Jackson State University